Addendum No. 1

RFP 24-02

Date: 01/09/2025

Date:  January 26, 2016

Clarifications:

- The Proposals Due Date has been shifted from January 14, 2025 to January 21, 2025 at 1:00pm.

January 21, 2025:	Proposals due at 1:00 PM SHARP, Yuba Community College District, District Offices Location: Sutter Center, District Offices, Second Floor, Room 217, Attention: David Willis, 3301 East Onstott Road, Yuba City, Ca., 95991.  There will be a public bid opening on this RFP in room 211 at the Sutter Center Building.

- Question/Statement:  The RFP states that: “The Engineering Enterprise (TEE) (Danny McKevitt) has completed a Yuba College Campus-wide electrical distribution systems assessment/inventory and has generated an Equipment and Conductor/Wiring Risk Matrix that has prioritized what should be considered to be upgraded in the Phase I scope of work.”

Answer:  Correct.  This document is in the link attachments in the RFP.

- Question/Statement:  The RFP states that this is Phase I and to consult  “Equipment and Conductor/Wiring Risk Matrix” for scope of work  Will Phase 1 include:

- High Priority Only?

Answer:  Yes, TEE will provide recommendations and the District/College will collaborate on which items will be included in the Phase I scope of work based on risk and impact as well as budgetary constraints.

- High and Medium Priority?

Answer: Please refer to 2.A answer above.

- High, Medium and Low Priority?

Answer: Please refer to 2.A answer above.

- Question/Statement: There is some additional areas of concern called out in earlier reports which are not in the “Equipment and Conductor/Wiring Risk Matrix”

Does the scope in the “Equipment and Conductor/Wiring Risk Matrix” supersede the 11/20/23 Tee Report and ATE Thermal Scan report?

Answer:  No. The ATE Thermal Scan Report items are being addressed now by the District/College and will not be part of the scope of work of Phase I.

Question:  Or should this scope be included Here are some examples, not a comprehensive list.

- TEE 11/20/23 report

Answer: See answers above.

  - Recommends replacement of a transformer in 100A not listed in risk evaluation matrix

Answer:  See answers above.  TEE and the District will determine the scope of phase I after further evaluation and discussion based on accurate cost estimates for items in the risk matrix and on risk and impact of potential failures.

  - Recommends replacement of 100B DPA panel not listed in risk evaluation matrix

Answer:  See answers above.  TEE and the District will determine the scope of phase I after further evaluation and discussion based on accurate cost estimates for items in the risk matrix and on risk and impact of potential failures.

- Question/Statement: ATE Thermal Scan

  - Recommends Torque Testing, breaker cycling,  and resurveying multi locations

Answer: The District has hired TEE to complete the development of a District-wide Electrical Distribution System Preventative Maintenance Plan that will then be bid as a separate project/service from the scope of this phase I Electrical Distribution System Upgrade project at Yuba College campus.

  - Points out Damaged/Melting CT

Answer:  See above answer under B.a.

- Question/Statement: Confirm cost estimating is only for Phase 1.

Answer: No. Cost estimating is for all items listed in the Risk/Matrix developed by TEE.

The End.